## Cover
Disinfection CT (Chlorine Contact)
Chlorine contact time and CT by the US EPA SWTR method — [1]
Version 0.1 · Generated 2026-10-21
Read first
This is a guided engineering calculation workbook, not a stamped design document.
Fill only yellow Input cells. Calculated and result cells are protected-by-convention (never hand-edit).
Review the Checks sheet — address any WARN or FAIL before use.
Enter governing code/table values (e.g. ampacity tables, demand factors, U-values) from your governing standard where a Source column asks for it.
Verify all results against project data and applicable standards with a qualified engineer.
Workbook structure
Inputs — every user entry (yellow).
Calculations — transparent formulas with reference IDs.
Outputs — final results (blue).
Checks — PASS/WARN/FAIL verification vs the reference limits.
Reference — sources cited by ID ([1], …).
Notes & Assumptions — declared limitations and assumptions.
Method
Chlorine contact time and CT by the US EPA SWTR method
EngiMetric · https://engimetric.com

## Summary
Disinfection CT (Chlorine Contact)
Master verdict | PASS
Key inputs
Free chlorine residual C | 1.2 | mg/L
Baffling factor (T10/TDT) | 0.7 | —
Required CT (regulatory) | 396 | mg·min/L
Key outputs
Effective contact time | 336 | min
Achieved CT | 403.2 | mg·min/L
Checks at a glance
Achieved CT ≥ required CT | PASS
Baffling factor in range | PASS
Version 0.1 · EngiMetric workbook library

## Inputs
Inputs — yellow cells: enter your values; source prompts governing choices
Free chlorine residual C | 1.2 | mg/L | operating residual
Contact volume | 800 | m³ | basin dimensions (effective)
Peak flow | 100 | m³/h | peak throughput
Baffling factor (T10/TDT) | 0.7 | — | basin baffling efficiency
Required CT (regulatory) | 396 | mg·min/L | EPA SWTR CT table (enter your governing value)

## Calculations
Calculations — transparent formulas; [n] is the reference ID (see Reference sheet)
Theoretical detention time | 8 | h | [1]
Effective contact time T10 | 336 | min | [1]
Achieved CT | 403.2 | mg·min/L | [1] — CT = C × T10

## Outputs
Outputs — final results (formula-driven; never hard-typed)
Effective contact time | 336 | min | [1]
Achieved CT | 403.2 | mg·min/L | [1]
Required CT (entered) | 396 | mg·min/L | [1]

## Checks
Checks — each row must land PASS (WARN acceptable when documented)
Achieved CT ≥ required CT | CT ≥ CTreq | PASS | [1]
Baffling factor in range | 0 < BF ≤ 1 | PASS | [1]
POE residual guidance (SWTR) | ≥ 0.2 mg/L | PASS | [1]
Required CT entered | > 0 | PASS | [1]
Master verdict
Overall result | PASS when every check passes | PASS

## Reference
References
[1] | US EPA Surface Water Treatment Rule and disinfection profiling guidance (CT method)
Equations used
Contact time and CT | T10 = (V/Q)·BF; CT = C × T10

## Notes & Assumptions
Notes & Assumptions
1. Required CT is a governing regulatory value entered by the user for their organism/temperature/pH combination — never invented here.
2. CT tables vary with organism, disinfection type, temperature and pH; the 0.2 mg/L minimum residual at POE is SWTR guidance.
Disclaimer
Governed by the EngiMetric Workbook Standard v1.0. Values computed depend entirely on the data entered.
Code/table-derived factors are user inputs prompted by their Source column — no copyrighted tables are embedded.
Not a substitute for qualified, licensed engineering review.