## Cover
RO Mass Balance
RO mass & salt balance by flow conservation — [1], [2]
Version 0.1 · Generated 2026-10-21
Read first
This is a guided engineering calculation workbook, not a stamped design document.
Fill only yellow Input cells. Calculated and result cells are protected-by-convention (never hand-edit).
Review the Checks sheet — address any WARN or FAIL before use.
Enter governing code/table values (e.g. ampacity tables, demand factors, U-values) from your governing standard where a Source column asks for it.
Verify all results against project data and applicable standards with a qualified engineer.
Workbook structure
Inputs — every user entry (yellow).
Calculations — transparent formulas with reference IDs.
Outputs — final results (blue).
Checks — PASS/WARN/FAIL verification vs the reference limits.
Reference — sources cited by ID ([1], …).
Notes & Assumptions — declared limitations and assumptions.
Method
RO mass & salt balance by flow conservation
EngiMetric · https://engimetric.com

## Summary
RO Mass Balance
Master verdict | PASS
Key inputs
Feed flow Qf | 100 | m³/h
Recovery Y | 75 | %
Key outputs
Permeate flow | 75 | m³/h
Concentrate flow | 25 | m³/h
Checks at a glance
Recovery within 90% limit | PASS
Flow balance closes (0.5%) | PASS
Salt balance closes (0.5%) | PASS
Version 0.1 · EngiMetric workbook library

## Inputs
Inputs — yellow cells: enter your values; source prompts governing choices
Feed flow Qf | 100 | m³/h | operational data
Recovery Y | 75 | % | design target (≤ 90)
Feed TDS Cf | 35000 | mg/L | feedwater analysis
Permeate TDS Cp | 350 | mg/L | projection or test data

## Calculations
Calculations — transparent formulas; [n] is the reference ID (see Reference sheet)
Permeate flow Qp | 75 | m³/h | [1] — Qp = Qf·Y/100
Concentrate flow Qc | 25 | m³/h | [1] — Qc = Qf − Qp
Salt passage SP | 1 | % | [1] — SP = Cp/Cf×100
Concentrate TDS Cc | 138950 | mg/L | [1] — salt balance: Qf·Cf = Qp·Cp + Qc·Cc
Flow balance error | 0 | m³/h | [1] — ≈ 0
Salt balance error | 0 | mg/L·m³/h | [1] — ≈ 0

## Outputs
Outputs — final results (formula-driven; never hard-typed)
Permeate flow | 75 | m³/h | [1]
Concentrate flow | 25 | m³/h | [1]
Concentrate TDS | 138950 | mg/L | [1]
Salt passage | 1 | % | [1]

## Checks
Checks — each row must land PASS (WARN acceptable when documented)
Recovery within 90% limit | ≤ 90% | PASS | [2]
Flow balance closes (0.5%) | ¦err¦ ≤ 0.5%·Qf | PASS | [1]
Salt balance closes (0.5%) | ¦err¦ ≤ 0.5%·Qf·Cf | PASS | [1]
Permeate TDS below feed TDS | Cp < Cf | PASS | [1]
Concentrate TDS above feed TDS | Cc > Cf | PASS | [1]
Master verdict
Overall result | PASS when every check passes | PASS

## Reference
References
[1] | Dupont Water Solutions, RO system design basics (method-level)
[2] | EngiMetric RO toolkit — maximum recovery constant (90%)
Equations used
Permeate and concentrate flows by recovery | Qp = Qf·Y/100; Qc = Qf − Qp
Concentrate TDS from salt conservation | Qf·Cf = Qp·Cp + Qc·Cc

## Notes & Assumptions
Notes & Assumptions
1. Flows and TDS must be unit-consistent; the workbook does not convert units.
2. Mass and salt closures are arrangement checks, not membrane performance attribution.
3. Recovery limit 90% is the engine constant; system-specific limits may be lower.
Disclaimer
Governed by the EngiMetric Workbook Standard v1.0. Values computed depend entirely on the data entered.
Code/table-derived factors are user inputs prompted by their Source column — no copyrighted tables are embedded.
Not a substitute for qualified, licensed engineering review.